A&E SPECIFICATIONS

9621AY / 9622AY   4-/8-CHANNEL OPTICAL DUPLEX OPTION MODULE HOST CARDS
and
9621AT/R / 9622AT/R   4-/8-CHANNEL OPTICAL SIMPLEX OPTION MODULE HOST CARDS
DIVISION 28__28 23 00 VIDEO SURVEILLANCE
LEVEL 1__28 23 23 VIDEO SURVEILLANCE SYSTEMS INFRASTRUCTURE

PART 2 – PRODUCTS
2.1	GENERAL
A.	TKH Security Solutions (www.tkhsecurity.com) is the manufacturer of these 4-/8-channel optical duplex and simplex Option Module host cards.
B.	TKH Security Solutions shall produce this product within a quality system in compliance with the ISO-9001.
C.	All equipment and materials used shall be standard components that are regularly manufactured and used in the manufacturer’s system.
D.	All systems and components shall have been thoroughly tested and proven in actual use.
E.	All systems and components shall be provided with comprehensive repair and spare parts replacement. The manufacturer on warranty and non-warranty items shall guarantee the spare parts and the repair.
F.	Use of substitutions shall void the warranty. 
2.2	Product DescriptioN
A.	The 9621AY, 9622AY, 9621AT/AR and 9622AT/AR Option Module host cards shall provide optical transport for four or eight duplex Option Module channels.
B.	These cards shall make complex system configuration easy by supporting nearly any combination of four or eight data, audio, contact closures, or intercom channels on a fiber.
C.	These cards shall also provide:
1. 	Transport of four or eight Option Module channels on one fiber
2.	Availability of Option Module for audio, data, contact closure, and intercom applications
3.	Network Management System (NMS) compatibility
D.	These units shall be built for rack-mounting.
1.	Rack-mount units shall be compatible with a 9002, 9008, or equivalent, power supply cabinet.
2.	Rack-mount units shall be configurable to stand-alone by using a 9003-2 mini-chassis or equivalent.
2.3	Design and Performance Criteria
A.	The 9621AY/9622AY and 9621AT/AR / 9622AT/AR multiplexer/demultiplexers shall link combine and separate data from four or eight Option Modules for transmission via one optical fiber. 
B.	The four or eight input channels shall be combined using TDM techniques into a 15 mbps data stream modulated onto the fiber. At the other end of the link, the 9621AY or 9622AY shall separate the four or eight channels and routes them to the four or eight Option Modules.
C.	The 96xxAT/AR units shall transmit data in one direction from the transmitter to the receiver over one fiber. A pair of 96xxAY units shall transmit data in both directions over one fiber. 
D.	9621AY and 9622AY cards shall be available in selected CWDM versions for use in SpectraStream 128 CWDM applications. 

E.	Option Module compatibility:
1.	9621AT and 9621AR cards shall be compatible with any Option Module except type F (FM Data Option Module). 
2. 	9621AY and 9622AY cards shall be compatible with any Option Modules including the GM and GR (AiPhone Intercom Series Interface Option Modules). 
3.	9622AT and 9622AR cards shall be compatible with any Option Module except type F (FM Data Option Module).
F.	All cards shall be rack-mount, plug-in cards that occupy a single slot in a Series 9000 card chassis. Each shall operate on 6VDC from the chassis power supply.
G.	These cards shall consume, depending on model, from 6 VDC via the chassis backplane 
H.	These cards shall operate through a wide temperate range (-40° to +74° C / -40° to +165  F).
I.	These cards shall hold UL safety certification, and meet CE and FCC part 15 immunity and emissions requirements.
2.4	Option Module
A.	Module A	1x Duplex Audio Channel
B.	Module B	1x Duplex user selectable RS-232, RS-422, 2- or 4-wire RS-485, or Manchester Data channel
C.	Module C	1 x Duplex contact closure channel 
D.	Module D 	2x Simplex stereo audio channels, TX End
E	Module E	2x Simplex stereo audio channels, RX End
F.	Module GM or GR	AiPhone Intercom Models (LE remotes, LEF and LEM masters)
2.5	Power Requirements 
A.	9621AY / 9621AT/AR versions
	1.	Voltage 	6 VDC (chassis)
	2.	Current	400-800 mA (depends on number and type of module installed)
B.	9622AY / 9622AT/AR versions
	1.	Voltage 	6 VDC (chassis)
	2.	Current	800-1000 mA (depending on number and type of Module installed)
2.6	Indicators 
A. 	9621AY/9622AY	Power, Sync, Not Sync, Loop
B.	9621T/9622T	Power
C.	9621R/9622R	Power, Sync, Not Sync
2.7	Management system
A.	Management System	9900 Network Management System (NMS)
2.8	PHYSICAL
A.	9621AY / 9621AT/R
	1.	Mounting	1-slot card, 9000 series chassis
	2.	Dimensions (H x W x D) 	154.9 x 20.3 x 218.4 mm (6.1 x 0.8 x 8.6 in.) 
	3.	Weight	227g (8 oz.)
B.	9622AY / 9622AT/R
	1.	Mounting	2-slot card, 9000 series chassis 
	2.	Dimensions (H x W x D) 	154.9 x 40.6 x 218.4 mm (6.1 x 1.6 x 8.6 in.) 
	3.	Weight	363g (12.8 oz.)
2.9	Environmental
A.	Operating temperature 	-40° C to +74° C (-40° F to +165° F)
B.	Storage temperature	-55° C to +85° C (-67° F to +185° F)
C.	Relative humidity 	<95% non-condensing
2.10	Optical
	9621AT/ 9622AT-S/LD-ST	9621AR/ 9622AR-S/LD-ST	9621AY-MM/
9622AY-MM TX/RX	9621AY-SM/
9622AY-SM TX/RX	
Fiber Type	MM(62.5), M(09)	MM(62.5), SM(09)	MM (62.5)	SM (09)	
Output Wavelength	850 nm, 1310nm	850nm, 1310 nm	850 nm, 1310 nm	1310 nm, 1550 nm	
Output Power 	16 dBm*, -7dBm	N/A	-16 dBm*, 17 dBm*	-7 dBm, -7 dBm	
Input Sensitivity	N/A 	-32 dBm*, -32 dBm 	-31 dBm, -31 dBm	-32 dBm, -32 dBm	
System Link Budget	N/A	16 dB, 25dB 
(TX to RX)	15 dB, 14 dB	25 dB, 25 dB	
Fiber Length (range)**	N/A	4 km, 62 km
(TX to RX)	4 km	62km	
Connector Type	ST (others optional)	ST (others optional)	ST (others optional)	ST (others optional)	
		* For 50/125 micrometer fiber, subtract 4 dB.
		**Range may be limited by modal and chromatic dispersion, fiber quality, and fiber bandwidth.
2.11	CERTIFICATIONS
A.	Regulatory	FCC part 15, CE, UL
2.12	WARRANTY
A.	5 years, parts and labor.
2.13	MODELS
A.	9621AY(XXXX)/MM-08T-ST		4-channel Option Module host card, A-side (1x MM)
B.	9621AY(XXXX)/MM-13T-ST		4-channel Option Module host card, B-side (1x MM)
C.	9621AY(XXXX)/SM-13T-ST		4-channel Option Module host card, A-side (1x MM)
D.	9621AY(XXXX)/SM-15T-ST		4-channel Option Module host card, B-side (1x SM)
E.	9622AY(XXXXXXXX)/MM-08T-ST	8-channel Option Module host card, A-side (1x SM)
F.	9622AY(XXXXXXXX)/MM-13T-ST	8-channel Option Module host card, B-side (1x MM)
G.	9622AY(XXXXXXXX)/SM-13T-ST	8-channel Option Module host card, A-side (1x SM)
H.	9622AY(XXXXXXXX)/SM-15T-ST	8-channel Option Module host card, B-side (1x SM)
I.	9621AT(XXXX)-S-ST		4-channel Option Module transmitter host card (1xMM)
J. 	9621AR(XXXX)-S-ST		4-channel Option Module receiver host card (1xMM)
K.	9621AT(XXXX)-L-ST		4-channel Option Module transmitter host card (1xSM)
L.	9621AR(XXXX)-L-ST		4-channel Option Module receiver host card (1xSM) 
M.	9622AT(XXXX)-S-ST		8-channel Option Module transmitter host card (1xMM)
N.	9622AR(XXXX)-S-ST		8-channel Option Module receiver host card (1xMM)
O.	9622AT(XXXX)-L-ST		8-channel Option Module transmitter host card (1xSM)
P.	9622AR(XXXX)-L-ST		8-channel Option Module receiver host card (1xSM)
	When ordering, replace (XXXX) with the identification letters of the four option modules being ordered.
2.14	RECOMMENDED Product Accessories
A.	9002 mount & power
	1.	9002 chassis	21-slot 19” rack-mount chassis 
	2.	9050BF power supply	100-240 VAC, 50/60 Hz input, 6.1 VDC output 
B. 	9008 mount with power	8-slot 2 RU 19” rack-mount power supply cabinet providing 100-240 VAC 50/60 Hz input, 6.1 VDC (nominal) output
C.	9003-2 mount & power	
	1. 	9003-2 chassis	2-slot mini chassis for stand-alone housing of rack-mount cards
	2. 	9010 power supply	100-240 VAC 50/60 Hz input, 6 VDC @ 4 A output