A&E SPECIFICATIONS

MC 10 and MC 11   19” POWER SUPPLY CABINETS
DIVISION 28__28 23 00 VIDEO SURVEILLANCE
LEVEL 1__28 23 23 VIDEO SURVEILLANCE SYSTEMS INFRASTRUCTURE

PART 2 – PRODUCTS
2.1	General
A.	TKH Security (www.tkhsecurity.com) is the manufacturer of these 19” power supply cabinets.
B.	TKH Security shall produce this product within a quality system in compliance with the ISO-9001.
C.	All equipment and materials used shall be standard components that are regularly manufactured and used in the manufacturer’s system.
D.	All systems and components shall have been thoroughly tested and proven in actual use.
E.	All systems and components shall be provided with comprehensive repair and spare parts replacement. The manufacturer on warranty and non-warranty items shall guarantee the spare parts and the repair.
F.	Use of substitutions shall void the warranty. 
2.2	PRoduct DESCRIPTION
A.	The MC 10 and MC 11 products shall be 19” power supply cabinets equipped to house and power TKH Security rack-mount modules. 
B.	All models of these cabinets shall provide:
1.	Powerful, efficient power, up to 105 watts, based on the latest switched-mode techniques.
2.	Stackablity for efficient use of space. 
3.	Reversible mounting brackets to allow for connections to be placed at either the front or the back.
4.	Two basic operating modes: SNM (also called EB-2) and EB-compatibility.
C.	Particular models of these cabinets shall offer:
1.	Power at either 230 VAC, 115 VAC, or 24 VDC.
2.	10 electrical slots or 11 electrical slots.
3.	Built-in fans sufficient to provide cooling for full-load operation over a wide temperature range. 
4.	Two programmable alarm contacts.
5.	Two DC inputs and two identical DC/DC conversion circuit, with include LED power failure indicator and galvanic isolated contact.
6.	Network management which shall provide status information and control over system modules, including the power supply cabinet itself. This network management shall be compatible with TKH Security’s Smart Network Manager (SNM™).
2.3	Design and Performance criteria
A.	The external bus of the power supply cabinet shall have either 10 or 11 free slots for TKH Security plug-in modules (7TE), supplying these with the correct DC voltages. 
B.	The “mains” power connector module (in dedicated power slot 0) shall contain a microprocessor, for use in:
1.	Status monitoring and controlling of SNM compatible modules in cabinet. 
2.	Controlling two relays.
3.	Reading status information of the cabinet proper, such as voltage.
C.	The two provided RS-485 serial bus interfaces to the processor shall allow for remote system management and control. Through these interfaces, a large number of these cabinets can be linked with shielded 4(+1 ground)-wire data cable (two twisted-pair cables). 
D.	The cabinet can be set to EB compatibility, using dip switches are used to set modes and parameters. The switches for setting the parameters of shall be located on the board inside the module in the dedicated slot 0.
E.	 These cabinets contains two independent power supplies operating in redundant fashion. If the active supply fails to meet its specifications, the other will take over automatically.
F.	The cabinets providing 230 or 120 VAC-powered internals shall be cooled with two fans. Cabinet construction shall allow for placement of mounting brackets on either the module side or on the fan side.
G.	These cabinets shall operate through a wide temperate range (-40° to +65° C / -40° to +149° F).
H.	These cabinets shall hold safety certifications including UL/IEC/EN 60950 (UL for MC 10 only) and IEC/EN 60825. They shall meet CE immunity and emissions requirements to include IEC/EN 61000, EN 50130-4, EN 50081-1, EN 55022, FCC Part 15, and RoHS.
2.4	Electrical
A.	Number of slots
	1.	MC 11	11 slots
	2.	MC 10	10 slots
B.	Type of slot	7 TE Eurocassette
2.5	Power Requirements
A.	Mains voltage 	
	1.	MC 10/11 AC-230	230 VAC
	2.	MC 10/11 AC-115	115 VAC
	3.	MC 11 DC	24 VDC
B.	Operation Voltage
	1.	MC 11 DC	15 to 30 VDC
C.	Frequency
	1.	MC 10/11 AC-230	40~100 Hz
	2.	MC 10/11 AC-115	40~100 Hz
D.	Maximum drop-out time
	1.	MC 10/11 AC-230	10 ms
	2.	MC 10/11 AC-115	10 ms
E.	Primary fuse
	1.	MC 10/11 AC-230	1.6A/250V slow
	2.	MC 10/11 AC-115	31.6A/250V slow 
F.	Power efficiency (full load)
	1.	MC 10/11 AC-230	~83%
	2.	MC 10/11 AC-115	>83%
	3.	MC 11 DC	>95%
G.	Output power
	1.	MC 10/11 AC-230	83W at 74 C ambient, 105W at 65 C ambient
	2.	MC 10/11 AC-115	83W at 74 C ambient, 105W at 65 C ambient
	3.	MC 11 DC	83W at 74 C ambient, 110W at 65 C ambient
H.	DC Input current
	1.	MC 11 DC	5A at 24 VDC or 8A at 15 VDC
2.6	Management 
A.	LED status indicators 
	1.	DC 	Power-on indicator (green)
	2.	EB	Data activity (SNM) on external bus (green)

B.	Network Management	SNM compatible
C.	SNM Variables	Voltage, modules, module temperature, module status, optical levels, etc.
	1.	SNM interfaces	1x 9-pin sub-D per cabinet
	2.	Interface format	RS-485
D.	Data rate	19.2 kb/s
E.	Programmable contacts	2 per cabinet
	1.	Switch rating	2A at 30 VDC
2.7	Environmental
A.	Operating temperature 	-40° C to +65° C (-40° F to +149° F)

B.	Storage temperature	-55° C to +85° C (-67° F to +185° F)
C.	Relative humidity 	<95% non-condensing
D.	MTBF 	>100,000h
2.8	MECHANICAL
A.	Dimensions (H x W x D)	
	1.	Without cabling	132 x 483 x 240 mm (5.2 x 19.0 x 9.4 in)
	2.	With cabling	132 x 483 x 350 mm (5.2 x 19.0 x 13.8 in)
B.	Weight (approx)	4.5 kg (9.9 lbs)
2.9	CERTIFICATIONS
A.	Regulatory, all models	FCC part 15, CE, RoHS 
D.	MC 10 only	UL
E.	Safety and EMC, all models	IEC/EN 60950, IEC/EN 60825, IEC/EN 61000, EN 50130-4, EN 50081-1, EN 55022 
2.10	WARRANTY
A.	5 years, parts and labor.
2.11	MODELS
A.	MC 11 AC-230	Power supply cabinet, 19”/3 RU
B.	MC 11 AC-115	Power supply cabinet, 19”/3 RU
C.	MC 11 AC-230 /EB-2	Power supply cabinet with SNM management interface, 
19”/3 RU
D.	MC 11 AC-115 /EB-2	Power supply cabinet with SNM management interface, 
19”/3 RU
E.	MC 10 AC-230 /EB-2	Dual power supply cabinet with SNM management, 19”/3 RU
F.	MC 10 AC-115 /EB-2	Dual power supply cabinet with SNM management, 19”/3 RU
G.	MC 11 DC-24V	Redundant DC power supply cabinet, 19”/3 RU